## General Calculations
Pulsation Dampener
Reciprocating Pump Sizing
Inputs
Is it a Grundfos Pump? |  | Yes? Click Here. | No? Use the below
Flow Rate | L/H |  | 300
Stroke Rate | SPM |  | 50
Operating Pressure | kPa |  | 1000
Fluctuation +/- | % |  | 2.5%
Gas Charge | Air / Nitrogen | Nitrogen | 0.714
Pump Type | K | Simplex; Single Acting | 0.6
Look up
Gas Charge | Polytropic Coefficient of Gas Expansion
Nitrogen | 0.714
Air | 1
Pump Type | Constant
Simplex; Single Acting | 0.6
Simplex; Double Acting | 0.25
Duplex; Single Acting | 0.25
Duplex; Double Acting | 0.15
Triplex; Single Acting | 0.13
Triplex; Double Acting | 0.06
Quadruplex; Single Acting | 0.1
Quadruplex; Double Acting | 0.06
Quintuplex; Single Acting | 0.06
Quintuplex; Double Acting | 0.02
Calculations
Flow Rate | L/min |  | 5
Volume / Stroke | L/stroke |  | 0.1
| USG / Stroke |  | 0.02642
| Cuinch/Stroke |  | 6.1024
Pmin | kPa |  | 975
| PSI |  | 141.412
Pmax | kPa |  | 1025
| PSI |  | 148.6639
P | Bar |  | 10
| PSI |  | 145.038
Volume Required | Cubic Inches |  | 213
| L |  | 3.49
Model |  |  | Sentry I Dome Top
AODD Sizing
Pump | Dampener Size Required
Port Size | Cubic Inch | L
1/4" | 10 | 0.17
3/8" | 10 | 0.17
DN15 | 36 | 0.59
DN20 | 85 | 1.4
DN25 | 85 | 1.4
DN32 | 175 | 2.87
DN40 | 175 | 2.87
DN50 | 370 | 6.07
DN80 | 1155 | 18.93
DN100 | 1155 | 18.93
DN40 | 175 | 2.87
Model |  | Sentry I Flat Top
Peristaltic Pump Sizing
Pump Model Lookup Chart
Pump |  |  | Dampener Size Required
Port Size | Gal(US) / Rev | L / Rev | Cubic Inch | L
1/4" | 0.004 | 0.02 | 10 | 0.17
3/8" | 0.004 | 0.02 | 10 | 0.17
DN15 | 0.0058 | 0.03 | 10 | 0.17
DN20 | 0.022 | 0.09 | 36 | 0.59
DN25 | 0.079 | 0.3 | 85 | 1.4
DN32 | 0.167 | 0.64 | 175 | 2.87
DN40 | 0.35 | 1.33 | 175 | 2.87
DN50 | 0.76 | 2.88 | 370 | 6.07
DN65 | 1.77 | 6.71 | 370 | 6.07
DN80 | 3.09 | 11.7 | 1155 | 18.93
DN100 | 5.28 | 19.99 | 1155 | 18.93
DN125 | 8.8 | 33.32 | 2310 | 37.86
DN150 | 8.8 | 33.32 | 2310 | 37.86
DN25 | 0.079 | 0.3 | 85 | 1.4
Model |  |  |  | Sentry II Dome Top
Inlet Stabilisation
Inputs
Flow Rate | L/H |  | 320
Stroke Rate | SPM |  | 200
Number of Pistons |  | One | 1
Acting |  | Single | 1
Calculation
Flow Rate | L/min |  | 5.3333
| L/Stroke |  | 0.026667
| Cubic Inch / Stroke |  | 1.6273
Lookup
Pistons
One | 1
Two | 2
Three | 3
Four | 4
Five | 5
Acting
Single | 1
Double | 2
Volume Required | Cubic Inches |  | 3.3
| L |  | 0.06
Model |  |  | Sentry III Flat Top
Surge Suppression
Inputs
Pipe | DN (mm) |  | 32
Flow Rate | L/s |  | 1.38
| m^3/s |  | 0.00138
Length of Pipe | m |  | 20
Design Pressure | kPa(g) |  | 1000
| psig |  | 145.0377
Maximum Pressure | kPa(g) |  | 1200
174.0453
Specific Gravity | # |  | 1
Pipe Cross Sectional Area | m^2 |  | 0.00080425
Fluid Velocity | m/s |  | 1.7159
| f/s |  | 5.6296
Density | kg/m^3 |  | 1000
| lbs/ft^3 |  | 62.428
Fluid Mass | kg |  | 16.085
| lbs |  | 35.4613
Fluid Volume | m^3 |  | 0.016085
| ft^3 |  | 0.56803
Gas Charge | Air / Nitrogen | Nitrogen | 1.4
Air | 1
Nitrogen | 1.4
(n-1)/n |  |  | 0.28571
Volume Required | Cubic Inches |  | 11
| L |  | 0.19
Model |  |  | Sentry II Flat Top
Pump Start Up and Shut Down
Inputs
Flow Rate | L/s
| GPM |  | 0
Length of Pipe | m
| Ft |  | 0
Design Pressure | kPa(g)
| psig |  | 0
Maximum Pressure | kPa(g)
| psig |  | 0
Speed of Sound in Fluid | m/s
| f/s |  | 0
Gas Charge | Air/Nitrogen |  | #N/A
Air | 1
Nitrogen | 1.4
| Part 1 |  | #DIV/0!
| Part 2 |  | #DIV/0!
| 1/Gas |  | #N/A
| Top Line |  | #DIV/0!
| Bottom Line |  | #DIV/0!
Volume Required | Cubic Inches |  | #DIV/0!
| L |  | #DIV/0!
Model |  |  | #DIV/0!
Thermal Expansion
Inputs
Initial System Pressure | kPa(g)
| psi(g) |  | 0
| psi(a) |  | 14.7
Maximum Pressure | kPa(g)
| psi(g) |  | 0
| psi(a) |  | 14.7
Initial System Temperature | Deg C
| Deg F |  | 32
Maximum Temperature | Deg C
| Deg F |  | 32
Cubic Expansion of Liquid / C | /C
| /F |  | 0
Linear Expansion of Pipe / C | /C
| /F |  | 0
Gas Charge | Air/Nitrogen |  | #N/A
Air | 1
Nitrogen | 1.4
Pipe Length | m
| Ft |  | 0
Pipe DN | mm
| Inches |  | 0
| Feet |  | 0
Excess Volume due to Expansion | Cubic Inches |  | 0
Volume Required | Cubic Inches |  | #N/A
| L |  | #N/A
Model |  |  | #N/A
If you are unsure of this calculation, or require pricing, please contact H2O Rx
Phone: | 0409 784 236
Email: | info@h2orx.com.au
Web: | www.h2orx.com.au
Note on D7: Scott Young: If unknown, use 100
Note on D9: Scott Young: 2.5% is a good guide
Note on C10: Scott Young: Use air to 1000 kPa Nitrogen above 1000 kPa
Note on D166: Scott Young: Water at 20 Deg C is 1481 m/s
This Pulsation Dampener sizing chart is based upon removing 93% of pulsation from the peristaltic pump.
If a higher degree of dampenening is desired, use the next largest size.
If you know the pump model, use the look up chart.
This Pulsation Dampener sizing chart is based upon removing 93% of pulsation from the air operated diaphragm pump. If a higher degree of dampenening is desired, use the next largest size.
This formula should be used in an application where water hammer is created from the use of a quick closing valve. The system piping should be straight with no elbows or change in pipe diameter - if otherwise, please call H2O Rx and submit a drawing of the system piping and valving.
This formula should be used in an application where water hammer is created from starting or stopping a pump. The system piping should be straight with no elbows or change in pipe diameter - if otherwise, please call H2O Rx. The Surge Suppressor's inlet must be at lleast equal to pipe diameter to insure unrestricted flow into it.

## Grundfos Pumps
Code | Prefix | Suffix | Model | Dampener Size (L) | Dampener Model | Notes
DDE | 6 | 10 | DDE 6-10 | 0.07 | Sentry III Flat Top
DDA | 7.5 |  | DDA 7.5- | 0.07 | Sentry III Flat Top | These are digital pumps and have very little pulsation
DDA | 60 | 10 | DDA 60-10 | 0.15 | Sentry III Dome Top | These are digital pumps and have very little pulsation
DDA | 200 |  | DDA 200- | 0.65 | Sentry II Dome Top | These are digital pumps and have very little pulsation
DDE | 6><30 |  | DDE 6><30- | 0.15 | Sentry III Dome Top | These are digital pumps and have very little pulsation
DMX | 221 | 4 | DMX 221-4 | 0.15 | Sentry III Dome Top
DMX | 221 | 8 | DMX 221-8 | 0.15 | Sentry III Dome Top
DMX | 221 | 9 | DMX 221-9 | 0.15 | Sentry III Dome Top
DMX | 221 | 12 | DMX 221-12 | 0.15 | Sentry III Dome Top
DMX | 221 | 14 | DMX 221-14 | 0.15 | Sentry III Dome Top
DMX | 221 | 16 | DMX 221-16 | 0.15 | Sentry III Dome Top
DMX | 221 | 18 | DMX 221-18 | 0.15 | Sentry III Dome Top
DMX | 221 | 26 | DMX 221-26 | 0.15 | Sentry III Dome Top
DMX | 221 | 27 | DMX 221-27 | 0.15 | Sentry III Dome Top
DMX | 221 | 35 | DMX 221-35 | 0.15 | Sentry III Dome Top
DMX | 221 | 50 | DMX 221-50 | 0.15 | Sentry III Dome Top
DMH | 251 | 10 | DMH 251-10 | 0.15 | Sentry III Dome Top
DMH | 252 | 10 | DMH 252-10 | 0.15 | Sentry III Dome Top
DMX | 221 | 17 | DMX 221-17 | 0.35 | Sentry II Flat Top
DMX | 221 | 25 | DMX 221-25 | 0.35 | Sentry II Flat Top
DMX | 221 | 39 | DMX 221-39 | 0.35 | Sentry II Flat Top
DMX | 221 | 60 | DMX 221-60 | 0.35 | Sentry II Flat Top
DMX | 221 | 75 | DMX 221-75 | 0.35 | Sentry II Flat Top
DMX | 221 | 115 | DMX 221-115 | 0.35 | Sentry II Flat Top
DDI | 222 | 60/150D | DDI 222-60/150D | 0.35 | Sentry II Flat Top | These are digital pumps and have very little pulsation
DME |  | 60/150 | DME -60/150 | 0.35 | Sentry II Flat Top | These are digital pumps and have very little pulsation
DMX | 226 | 42M | DMX 226-42M | 0.35 | Sentry II Flat Top
DMX | 226 | 100M | DMX 226-100M | 0.35 | Sentry II Flat Top
DMX | 226 | 142M | DMX 226-142M | 0.35 | Sentry II Flat Top
DMX | 226 | 67L | DMX 226-67L | 0.35 | Sentry II Flat Top
DMX | 226 | 132L | DMX 226-132L | 0.35 | Sentry II Flat Top
DMX | 226 | 190L | DMX 226-190L | 0.35 | Sentry II Flat Top
DMX | 226 | 253 | DMX 226-253 | 0.35 | Sentry II Flat Top
DMX | 226 | 82M | DMX 226-82M | 0.65 | Sentry II Dome Top
DMX | 226 | 160M | DMX 226-160M | 0.65 | Sentry II Dome Top
DMX | 226 | 230M | DMX 226-230M | 0.65 | Sentry II Dome Top
DMX | 226 | 95L | DMX 226-95L | 0.65 | Sentry II Dome Top
DMX | 226 | 199L | DMX 226-199L | 0.65 | Sentry II Dome Top
DMX | 226 | 280L | DMX 226-280L | 0.65 | Sentry II Dome Top
DMX | 226 | 130M | DMX 226-130M | 0.65 | Sentry II Dome Top
DMX | 226 | 255M | DMX 226-255M | 0.65 | Sentry II Dome Top
DMX | 226 | 380M | DMX 226-380M | 0.65 | Sentry II Dome Top
DMX | 226 | 152L | DMX 226-152L | 0.65 | Sentry II Dome Top
DMX | 226 | 321L | DMX 226-321L | 0.65 | Sentry II Dome Top
DMX | 226 | 460L | DMX 226-460L | 0.65 | Sentry II Dome Top
DMX | 226 | 249L | DMX 226-249L | 0.65 | Sentry II Dome Top
DMX | 226 | 525L | DMX 226-525L | 0.65 | Sentry II Dome Top
DMX | 226 | 800L | DMX 226-800L | 0.65 | Sentry II Dome Top
DMH | 254 | ??? | DMH 254-??? | 0.65 | Sentry II Dome Top | 50 to 291 L/H range
DMH | 255 | ??? | DMH 255-??? | 0.65 | Sentry II Dome Top | 194 to 550 L/H range
DME | 375 | ??? | DME 375-??? | 0.65 | Sentry II Dome Top | These are digital pumps and have very little pulsation
DMH | 255 | ??? | DMH 255-??? | 1.4 | Sentry II Dome Top | 194 to 550 L/H range
DME | 940 | ??? | DME 940-??? | 1.4 | Sentry II Dome Top | These are digital pumps and have very little pulsation
DMH | 257 | ??? | DMH 257-??? | 2.6 | Sentry I Flat Top | 220 to 1500 L/H range
DMX | 227 | ??? | DMX 227-??? | 5.6 | Sentry I Dome Top | 430 to 2000 L/H range
DMX | 227 | ???/2 | DMX 227-???/2 | 9.5 | Contact H2O Rx | 430 to 2000 L/H range. This is a duplex pump (two heads)
DMH | 257 | ???/2 | DMH 257-???/2 | 9.5 | Contact H2O Rx | 220 to 1500 L/H range. This is a duplex pump (two heads)
To size a dampener for a Grundfos pump, use the filters in the heading row to get the best match, read the dampener size and dampener model, then ask H2O Rx for a quote.

## Peristaltic
Perstaltic Pumps - Manufacturer Recommendations
Dampener Size CU Inch | Dampener Size L | WMB | Verder | Blackmer | Periflo | Larox | Eccentric
10 | 0.16 | SPX-10 | VF-10 | A10 | AMP10
10 | 0.16 |  |  |  | CT10
10 | 0.16 |  |  |  | AMP13
10 | 0.16 |  |  |  | CT13
36 | 0.59 | SPX-15 | VF-15 |  | AMP16
85 | 1.39 | SPX-20 | VF-25 | A20 | AMP19 | LPPD15 | SLP6
85 | 1.39 | SPX-25 |  | A25 | CT19 | LPPD20 | SLP10
85 | 1.39 |  |  |  | AMP22 |  | SLP13
85 | 1.39 |  |  |  | CT22 |  | SLP23
85 | 1.39 |  |  |  | RBT25 |  | SLP58
85 | 1.39 | [5 empty] | SLP128
85 | 1.39 | [5 empty] | SLP218
175 | 2.87 | SPX-32 | VF-32 | A40 | FMP30
175 | 2.87 | SPX-40 | VF-40 | AX40 | RBT32
175 | 2.87 |  |  |  | FMP40
175 | 2.87 |  |  |  | FMP50
175 | 2.87 |  |  |  | RBT40
370 | 6.07 | SPX-50 | VF-50 | AX65 | RBT60 | LPPT25 | SLP440
370 | 6.07 |  |  |  |  | LPPD25 | SLP654
370 | 6.07 |  |  |  |  | LPPT32
5 G | 18.93 | SPX-65 | VF-65 | A80 | RBT70 | LPPT40
5 G | 18.93 | SPX-80 | VF-80 |  |  | LPPT50
| 18.93 |  |  |  |  | LPPT65
10 G | 37.85 | SPX-100 | VF-100 | A100 |  | LPPT80
10 G | 37.85 |  | VF-125 | AS125